®

®

Spyder BACnet

Programmable Controllers

SPECIFICATION DATA

provides flexible, universal inputs for external sensors,

digital inputs, and a combination of analog outputs and

digital outputs.

The photo shown is the PVB6436AS, which includes the

Series 60 floating actuator.

FEATURES

•

•

Uses BACnet MS/TP network communication.

EIA-485 communications network. Capable of baud

rates between 9.6 and 115.2 kbits/s.

•

Capable of stand-alone operation, but can also use

BACnet MS/TP network communications.

•

•

Sylk™ bus for use with Sylk-enabled sensors.

APPLICATION

Support for up to 40 controllers per BACnet MS/TP

segment (under 30 is recommended).

The PUB and PVB controllers are part of the Spyder family.

The nine controllers are BACnet MS/TP network devices

designed to control HVAC equipment. These controllers

provide many options and advanced system features that

allow state-of-the-art commercial building control. Each

controller is programmable and configurable using the

NIAGARA FRAMEWORK® software.

•

•

Field configurable and programmable for control,

input, and output functions using the NIAGARA

FRAMEWORK® software.

Function Block engine, which allows the application

designer to program the controller to perform a wide

variety of HVAC applications.

The Spyder BACnet controllers require the Spyder BACnet

Programmable Feature to be licensed in the WEBpro

workbench tool and the WEBS AX JACE Controller for

programming and downloading. The Spyder BACnet Models

are also available as Individually Licensed Controllers (ILC).

The ILC versions are identical in design and capability in

every detail except for the licensing. The Individual

Licensing of the Spyder ILCs (the License is built in) allows

them to be programmed and downloaded with any brand of

the Niagara Workbench or JACE controller. The Spyder ILCs

are identified with a suffix on the Part Number of -ILC.

Example: PUB6438S-ILC follows all the same Installation

Instructions information as the PUB6438S.

•

•

Built-in Zone Control functions include a remote wall

module interface and a scheduler.

Pressure-independent or pressure-dependent single

or dual duct Variable Air Volume (VAV) control as well

as Unitary equipment control.

•

Microbridge air flow sensor with dual integral restric-

tor design (PVB0000AS, PVB4022AS, PVB4024NS,

PVB6436AS, and PVB6438NS).

•

•

Easy user access to air flow sensor inputs.

Actuator (PVB0000AS, PVB4022AS, and

PVB6436AS) mounts directly onto VAV box damper

shaft and has up to 44 lb-in. (5 Nm) torque, 90-

degree stroke, and 90 second timing at 60 Hz.

The controllers are for use in VAV (Variable Air Volume),

Unitary, and advanced HVAC control applications. Each

controller contains a host microcontroller to run the main

HVAC application and a second microcontroller for

BACnet MS/TP network communications. Each controller

•

•

All wiring connections are made to removable

terminal blocks to simplify controller installation and

replacement.

Both controller housing and actuator are UL plenum

rated.

63-1328-08

SPYDER® BACNET® PROGRAMMABLE CONTROLLERS

DESCRIPTION

The programmable VAV/Unitary controllers are available in three models, as described in Table 1.

Table 1. Controller Configurations.

UI

Programmable (Universal (Digital (Analog (Digital

Type Input) Input) Output) Output)

DI

AO

DO

Velocity Pressure

Sensor

(Microbridge)

Controller

Model

Series 60

Floating Actuator

PUB1012S

Unitary

1a

4a

0

1

2

4

8

NO

NO

PUB4024S

Unitary

0

2

NO

NO

NO

PUB6438S

PUB6438SR

PVB0000AS

PVB4022AS

Unitary

Unitary

VAV

6

4

4

0

0

3

3

0

2

NO

6

8 Relays NO

NO

0

0

2

YES

YES

YES

YES

VAV

4a

PVB4024NS

VAV

4a

0

2

4

YES

NO

PVB6436AS

PVB6438NS

VAV

VAV

6

6

4

4

3

3

6

8

YES

YES

YES

NO

a

One Universal Input (UI-1*) is user selectable as a fast digital pulse meter

SPECIFICATIONS

Electrical

Rated Voltage: 20-30 Vac; 50/60 Hz

Power Consumption:

100 VA for controller and all connected loads (including

the actuator on model PVB6436AS)

Controller only Load: 5 VA maximum; models PVB6438NS,

PUB6438S, and PUB6438SR

Controller and Actuator Load: 9 VA maximum; model

PVB6436AS

External Sensors Power Output: 20 Vdc ±10% @ 75 mA

maximum

Each controller is programmable because the user

chooses which function blocks to use and how to connect

them. It is configurable because each Function Block has

user-defined behavior.

The PVB6436AS and PVB6438NS models are Variable Air

Volume (VAV) controllers, and the PUB6438S and

PUB6438SR models are Unitary controllers.

VAV Equipment Control

(PVB0000AS, PVB4022AS,

PVB4024NS, PVB6436AS, and

PVB6438NS)

The VAV controllers provide pressure-independent air flow

control and pressure-dependent damper control. VAV

systems generally provide cool air only to zones. However,

each controller has additional programmable inputs and

outputs that may be used to control devices, such as a fan

or VAV box reheat coils. Heaters can be staged electric or

modulating hot water. Supply and exhaust pressurization

control are provided on a zone basis.

Environmental

VAV Operating & Storage Temperature Ambient Rating

(models PVB0000AS, PVB4022AS, PVB4024NS,

PVB6436AS, and PVB6438NS):

Minimum 32° F (0° C); Maximum 122° F (50° C)

Unitary Operating & Storage Temperature Ambient Rating

(models PUB1012S, PUB4024S, PUB6438S, and

PUB6438SR):

Minimum -40° F (-40° C); Maximum 150° F (65.5° C)

Relative Humidity: 5% to 95% non-condensing

Unitary Equipment Control

(PUB1012S, PUB4024S, PUB6438S, Dimensions (H/W/D)

and PUB6438SR)

See Fig. 1 to Fig. 4 beginning on page 6 for dimensioned

drawings.

PUB1012S, PUB4024S, and PVB4024NS:6.25 x 4.81 x

2.26 in. (15.92 x 12.20 x 5.74 cm)

PVB0000AS, PVB4022AS (including Actuator):

6.60 x 8.28 x 2.26 in. (16.70 x 21.10 x 5.74 cm)

PVB6436AS (including Actuator): 6.27 x 10.316 x 2.26 in.

(15.92 x 26.20 x 5.74 cm)

Unitary equipment includes natural convection units,

radiant panels, unit heaters, unit ventilators, fan coil units,

and heat pumps. Unitary equipment does not require a

central fan. Depending on design, unitary equipment may

perform one or all of the functions of HVAC—ventilation,

filtration, heating, cooling, humidification and

distribution. Unitary equipment frequently requires a

distribution system for steam or hot and or chilled water.

PVB6438NS: 5.76 x 6.85 x 2.26 in. (14.62 x 17.40 x 5.74 cm)

PUB6438S, PUB6438SR: 5.45 x 6.85 x 2.26 in. (13.84 x

17.40 x 5.74 cm)

63-1328—08

2